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Indoor Static Pressure Measurement Master Specification

Product:
Subject to compliance with requirements for pressure and flow meters in heating, ventilation, and air conditioning systems. American Made, Buy American Act FAR 52.225.1, field serviceable.
The basis of the design is the S.A.P., Shielded Static Air Probe. Manufacturers approved to bid must adhere to the requirements listed below.

Description:
[bookmark: _Hlk197521720]The sensors shall be capable of detecting and sending space-controlled pressure to a pressure transmitter to determine differential pressure between indoor areas.

Indoor Application:
Provide where indicated, a static pressure measurement/control system capable of continuously monitoring and controlling the differential pressure between indoor spaces. Each control system shall consist of shielded static air probe(s) and a transmitter. In order to guarantee the overall accuracy and performance of the static pressure measurement/control system, the probes and transmitter shall be by the same manufacturer.
Shielded Room and Space Static Pressure Sensors (S.A.P.)
For each room or space, a minimum of one shielded static pressure sensor shall be provided suitable for surface (recessed flush, suspended, junction box, external flush) mounting. Each pressure sensor shall contain multiple sensing ports, a pressure impulse suppression chamber, and provide airflow shielding. It shall be all contained in an aluminum casing (316 Stainless Steel optional) with brushed finish on exposed surfaces.
These probes shall be capable of sensing the static pressure in the proximity of the sensor to within ±1% of the actual value, readings not impacted when subjected to a maximum airflow of 1,000 FPM from a 360 radial source.
Preferred Model code is SAP/B, SAP/P, or SAP/S shielded static air probe.
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Warranty:
Each static pressure sensor shall be covered by a 1 year no-fault warranty and three-year manufacturer warranty.  

Installation:
Airflow measurement sensors and transmitters shall be installed per the manufacturer’s recommendations.

Model Code:
Preferred Model code for project _______________ is SAP/_______________
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