Indoor Static Pressure Measurement Master Specification

- Product:

  - Subject to compliance with requirements for pressure and flow meters in heating, ventilation, and air conditioning systems. American Made, Buy American Act FAR 52.225.1, field serviceable.

  - The basis of the design is the S.A.P., Shielded Static Air Probe. Manufacturers approved to bid must adhere to the requirements listed below.

- Description:

  - The sensors shall be capable of detecting and sending space-controlled pressure to a pressure transmitter to determine differential pressure between indoor areas.

- Indoor Application:

  - Provide where indicated, a static pressure measurement/control system capable of continuously monitoring and controlling the differential pressure between indoor spaces. Each control system shall consist of shielded static air probe(s) and a transmitter. In order to guarantee the overall accuracy and performance of the static pressure measurement/control system, the probes and transmitter shall be by the same manufacturer.

  - Shielded Room and Space Static Pressure Sensors (S.A.P.)

    - For each room or space, a minimum of one shielded static pressure sensor shall be provided suitable for surface (recessed flush, suspended, junction box, external flush) mounting. Each pressure sensor shall contain multiple sensing ports, a pressure impulse suppression chamber, and provide airflow shielding. It shall be all contained in an aluminum casing (316 Stainless Steel optional) with brushed finish on exposed surfaces.

    - These probes shall be capable of sensing the static pressure in the proximity of the sensor to within ±1% of the actual value, readings not impacted when subjected to a maximum airflow of 1,000 FPM from a 360 radial source.

    - Preferred Model code is SAP/B, SAP/P, or SAP/S shielded static air probe.

Rev A

DOC-0007819

- Warranty:

  - Each static pressure sensor shall be covered by a 1 year no-fault warranty and three-year manufacturer warranty.

- Installation:

  - Airflow measurement sensors and transmitters shall be installed per the manufacturer’s recommendations.

- Model Code:

  - Preferred Model code for project _______________ is SAP/_______________

DOC-000XXXX

Rev A