Outdoor Static Pressure Measurement Master Specification

- Product:

  - Subject to compliance with requirements for pressure and flow meters in heating, ventilation, and air conditioning systems. American Made, Buy American Act FAR 52.225.1, field serviceable.

  - The basis of the design is the S.A.P, Shielded Static Air Probe and S.O.A.P, Shielded Static Outside Air Probe. Manufacturers approved to bid must adhere to the requirements listed below.

- Description:

  - The sensors shall be capable of detecting and sending space-controlled pressure to a pressure transmitter to determine differential pressure between indoor space(s) and the outdoors.

- Application:

  - Outdoor Applications:

    - Provide where indicated, a static pressure measurement/control system capable of continuously monitoring and controlling the differential pressure between indoor spaces(s) and the outdoors. Each control system shall consist of shielded static air probes for indoor locations, a shielded static outside air probe for outdoor locations, and a transmitter. In order to guarantee the overall accuracy and performance of the static pressure measurement/control system, the probes and transmitter shall be by the same manufacturer.

    - Shielded Static Outside Air Probe (S.O.A.P)

      - Provide for the Static Pressure Measurement/Control System an outdoor static pressure sensor constructed of 10 ga. Type 316 stainless steel with a 2" diameter FPT connection.

      - The outdoor air probe(s) shall be capable of sensing the outside atmospheric air pressure to within 2% of the value, readings not impacted when subjected to radial wind velocities up to 40 miles per hour with approach angles up to 30º to the horizontal.

      - Preferred Model code is S.O.A.P Shielded Static Outside Air Probe.

    - Shielded Room and Space Static Pressure Sensors (S.A.P)

DOC-0007820

Rev A

For each room or space, a minimum of one shielded static pressure sensor shall be provided suitable for surface (recessed flush, suspended, junction box, external flush) mounting. Each pressure sensor shall contain multiple sensing ports, a pressure impulse suppression chamber, and provide airflow shielding. It shall be all contained in an aluminum casing (316 Stainless Steel optional) with brushed finish on exposed surfaces.

      - These probes shall be capable of sensing the static pressure in the proximity of the sensor to within ±1% of the actual pressure value, readings not impacted when subjected to a maximum airflow of 1,000 FPM from a 360 radial source.

      - Preferred Model code is SAP/B, SAP/P, or SAP/S shielded static air probe.

- Warranty:

  - Each transmitter shall be covered by a 1 year no-fault warranty and three-year manufacturer warranty.

- Installation:

  - Airflow measurement sensors and transmitters shall be installed per the manufacturer’s recommendations.

- Model Code:

  - Preferred Model code for project _______________ is SAP/_______________

  - Preferred Model code for project _______________ is SOAP/_______________